## Slide 1
Accelerator Capabilities Enhancement (ACE) Workshop
Main Injector Controls and Instrumentation
Kyle J. Hazelwood
January 30, 2023

## Slide 2: Outline
Criteria
Upgrades and Enhancements
Summary

## Slide 3: Criteria
  2 MW MI Fast Ramp Proposal 2MW
      Is enhancement or upgrade necessary or desirable for proposal
  PIP-II PIPII
      Is enhancement or upgrade necessary or desirable for PIP-II era
  Reliability R
      Would enhancement or upgrade significantly increase uptime or lower maintenance and upkeep
  Sustainability S
      Would enhancement or upgrade make operations more sustainable (less energy, less waste, smaller environmental impact)
  Performance P
      Would enhancement or upgrade increase operations performance (more beam, more efficiently)
    Criticality C[0-3]
      How critical is this item to present or future operations
    Cost $[1-3]
      Relative estimate of cost
    Labor L[1-3]
      Relative estimate of labor

## Slide 4: Main Injector Power Supply Controls
  Most of the Main Injector main power supply controls are original to 1990’s construction
  PS PLCs (2MW, R, C3, $2, L2)
      50 (24 just for MI quad and bend supplies)
      $150k, 800 hrs
  PS PLC Control Power (2MW, R, C3, $1, L2)
    10 (8 remaining)
    $56k, 320 hrs
  DC PS Control Communications (2MW, R, C3, $1, L2)
    ~$50k, ~100’s hrs
  Bus DCCTs (2MW, R, C3, $2, L?)
    7
    ~$112k
  PS Data Link (2MW, R, C3, $1, L?)
    CAMAC based
  MECAR (2MW, R, S, P, C3, $1, L2)
    VME based
    Sustainability opportunity

## Slide 5: Water Cooling Controls
  Main Injector water cooling controls needs to be replaced
  House PLCs (2MW, R, C3 , $2, L2)
    Magnet, RF, Cavity systems
    SixTrack system obsolete
  House VMEs (2MW, R, C3 , $1, L1)
  Advantage Starter Cards (2MW, R, S, C3, $2, L2)
    ~50 between LCW and pond pumps
    Obsolete
    Some pond have been replaced with Variable Frequency Drives (VFD)
      VFD offer new way to regulate LCW temperature while lowering energy use

## Slide 6: Vacuum Controls
  All Main Injector, 8 GeV and 1/3 of Recycler running on obsolete CIA system
  Ion Pump PS (PIPII, R, S, P, C3 , $3, L3)
      ~500
      ~$500-750k, 1000 hrs
      Networked Ethernet IPs in use in Recycler
  Beam Valve Control (PIPII, R, C3, $1, L2)
    ~1-2 per house
    ~$100k, ~250 hrs
    Need to replicate CIA crate beam valve control, sector permit
    Could be used to increase IP vacuum readback frequency

## Slide 7: Field Bus
  Much of the PS ramp waveforms, timing, clock, signals, ADC, machine protection is handled via CAMAC, a 1970’s tech
  CAMAC Cards (R, P, C3, $3, L3)
      ~603,
      ~$2M+, 1000’s hrs
    CAMAC Crates (R, P, C3, $3, L3)
      `~88
      ~$1M
    CAMAC VME Front Ends (R, P, C2, $1, L1)
      4
      ~$50k
    CAMAC ADC (R, P, C1, $2, L2)
      Need more channels, less multiplexed
        We can’t currently read adjacent corrector currents in Recycler
      Greater resolution

## Slide 8: Software
  Many client applications were originally written 25+ years ago
  Client Applications (R, P, C2, $1, L3)
    Console Programs, Comfort Displays
      ~100 for Main Injector, Recycler, 8 GeV
      1000’s hrs
    More Data (P, S, C1, $?, L2)
      More resolution
      Better timestamp synchronization
      More waveform data
    Data Logging (R, P, S, C2, $2, L2)
      We save a very small fraction of our machine data
      ~5 TB per day to save all existing readbacks
    Issue tracking (R, P, S, C1, $1, L1)
      Elog is great , but does a poor job of tracking resolution of issues that take longer than a few shifts
    APIs (R, P, S, C1, $1, L1)
      Convenient, intuitive, flexible access to machine data and machine settings

## Slide 9: RF Controls
  Most RF controls are in need of replacement
  LLRF VXI Crates (2MW, PIPII, R, P, C3 , $2, L2)
    Needed for Main Injector and Recycler
    HLRF IRM Nodes (2MW, PIPII, R, P, C3 , $2, L2)
      44
      Proposed PiRM nodes
    Anode Controls (2MW, PIPII, R, P, C3 , $1, L2)
    Damper Controls (PIPII, R, P, C3 , $2, L2)

## Slide 10: Beam Instrumentation
  Much of our beam instrumentation is EOL. Most systems were designed for manual tuning and studies
  Beam Position Monitors (PIPII, R, P, C3, $3, L2)
    8 GeV, Recycler, MI
    Digitizers obsolete, few spares
    VME based
  Beam Loss Monitors (PIPII, R, P, C3, $3, L2)
    Ionization chambers need refurbishment
    VME based
  Wire Profile Monitors (PIPII, R, P, C3, $2, L2)
    Motion controls need refurbishment
    Better wire frame, can designs desired
      Bias planes, dual planes, C-channels
    SWIC scanner + VME FE scheme dated
  Ion Profile Monitors (PIPII, R, P, C1, $2, L2)
    Fast HV switch to preserve Micro channel plate lifetime

## Slide 11: Beam Instrumentation (Continued)
  Toroids (PIPII, R, P, C2, $2, L2)
    VME/NIM based
  Beam Intensity DCCT (PIPII, R, P, C3, $2, L2)
    VME based
    Hardware is approaching beam intensity limits for PIP-II
  More Non-invasive Measurements (PIPII, R, P, C2, $3, L2)
    Electron beam profile monitor?
    Halo profile monitors?
    Tune measurement?

## Slide 12: Automation
  The vast majority of Main Injector, Recycler and 8 GeV are tuned manually.
  Orbit Control (2MW, PIPII, R, P, C3 , $1, L2)
    More autotunes
  Tune Control (2MW, PIPII, R, P, C3 , $2, L2)
    Need active tune readback (Dampers?)
  Artificial Intelligence, Machine Learning (2MW, PIPII, R, P, S, C3 , $2, L2)
    Anomaly Detection
      Tuning, studies are often hampered by broke instrumentation only discovered in post
    Multi-objective Optimization
      Optimize the machine using multiple sub-systems for multiple objectives
    Better regulation schemes
      Slow spill duty factor
      Main Injector ramp regulation
      Energy savings
    Inference, realtime diagnostics
    Digital Twins (better machine models)
    Natural Language Processing (Elog searches?)
  Automated Tunnel Surveys, Robotics (2MW, PIPII, R, P, S, C3, $2, L2)

## Slide 13: Miscellaneous
  Not every needed upgrade fits into a neat category
  Computer Room (2MW, PIPII, R, P, C3 , $3, L2)
    Limited cooling
    At max capacity
    Generator needed
  Kautz Road Sub-station (KRS) Controls (2MW, R, P, C3 , $2, L2)
  Building Monitoring/Metering (R, P, S, C3 , $2, L2)
    Opportunity for sustainability
  Cabling Replacement (2MW, PIPII, R, P, S, C3 , $3, L3)
    Radiation damaged cables, cable liftetimes
    Investigate other insulation materials
  Motion Controls (R, P, C3 , $2, L2)
    Main Injector, Recycler, 8 GeV Collimators
    Wire Profile Monitors
    Ion Profile Monitors
    Septa tanks
    Crawling Wire
  Total Loss Monitors (2MW, PIPII, R, S, C2, $2, L2)

## Slide 14: Summary
  There are no obvious Controls or Instrumentation technological obstacles that would prevent the 2 MW Fast Ramp Upgrade
    Just a matter of resources and support
  Increasing reliability should be prioritized the same as any increase in Main Injector duty factor or beam intensity
  Majority of Main Injector controls is EOL, there is much that should be replaced/upgraded
  Much of our instrumentation is oriented towards manual tuning and studies
    Need more focus on providing streaming readings for future automation
  While both Main Injector and Recycler currently have beam transmission efficiencies of ~98%, this may be insufficient for future machine operations
    Tunnel activation, personnel exposure
    Component lifetimes
  More effort and support should be given to machine automation to help improve overall machine efficiencies
    AI/ML has great promise
  Opportunities exist, and should be explored to increase Main Injector sustainability
  Need to actively rotate out aged systems
    Attracting and retaining talent is already hard, few want to work on dated systems
  More investigation is needed to adequately scope costs and labor
    ACORN is doing some of this investigation already
  This amount of work will require significant increases in personnel and funds