## Slide 1
Geoff Savage
04 June 2023
2x2 Network and Computing Status

## Slide 2: 2x2 Rack Locations – Final???
Beam Direction

## Slide 3: 2x2 Rack Locations
Beam Direction
Not all racks in the image are scheduled to be installed for the initial phase of 2x2.
Platform rack hidden behind light adc rack in this view.

## Slide 4: Rack List
Electronics
  Purity Monitor
  Light ADC
  Power Supply
  HV Filter and Light VGA (on platform)
Server Racks
  Server 1,2,3 for 14 Linux servers
    Server 1 rack – 48-port 1 Gb copper switch for all Linux servers
    Server 2+3 racks have no network switches
  Server 4+5 racks are for expansion if needed
    Electrical outlets will be installed but not used right away
Network rack
  Main switch (router) – 48 port SFP+
Cryo rack
Minerva
  Light Injection (LI)
  Readout

## Slide 5: 2x2 Rack Locations
Beam Direction

## Slide 6: 2x2 Rack Locations
Beam Direction

## Slide 7: Upper Wire Way Outlets
L6-20-R Outlet
not 30A

## Slide 8: Outlets Over Network Rack

## Slide 9: Overview
Minerva readout is working (Server 1 rack)
  Two gateway servers
  Two DAQ servers – connect to Minerva VME readout crate
  24-port network switch installed in server 1 rack (borrowed)
  Network fuse panels in Minerva LI rack are on the network
2x2 Networking
  Switches are here
    Ordered 17-Oct-2022
    PO 693151
  Most cabling is in hand
    RITM1635011 - Cabling for 2x2 demonstrator network installation in Minos underground
    What we are missing has been ordered by Networking
  Transceivers are available
  Installation
    Only have power for the Network and Server 1 racks
    Requested installation of the router and 1 Gb switch sometime in the the first two weeks of June
    Not sure of the status with the safety stand down and illness of group leader
2x2 Computing
  Servers are on site
  2x2 DAQ (5) – 4 DAQ and 1 slow controls
  Minerva DAQ (3) – One used for nearline
  Operations (4) – new gateways and remote desktops
  Already have two gateways installed in Server 1 rack

## Slide 10: Cabling (not to scale)
catwalk
Minerva LI
Quiet power
copper from server 1 rack
Power Supply
Detector Power
12-port managed switch
Minerva Readout
Quiet power
no network devices
Cryo Rack
EPP power
Computer
UPS
Network
EPP power
48-port router
SFP+ ports
UPS
Light ADC
Detector Power
12-port managed switch
Purity Monitor
Detector Power
12-port managed switch
Server1
Quiet power
Minerva DAQ servers, gateways
48-port managed switch 1 Gb copper
Server2
Quiet power
AC2x2 DAQ servers
Cryostat
Platform Rack
Detector Power
48-port managed switch
Electrical Requirements:
Fiber separates grounds.
No copper between racks on different power.
MND 102
No Power
Trunk
Fiber
x9 for
light
Fibers from racks go
back to Network Rack.
Within each rack copper
from 12-port switch to
each device.
Server3
Quiet power
AC2x2 DAQ servers
x4 for
light
Light ADC has
independent network.
10Gb copper
1Gb copper
fiber
Key:

## Slide 11: 2x2 Demonstrator Network (Logical)
2x2 DAQ (x4)
Slow Controls
Minerva (x3)
Operations (x4)
2x2 Public
(10 Gb)
Light Readout
(10 Gb)
2x2 Private
(1Gb)
LRO VME (x9)
Slow controls
IPMI
Network Rack
(Router)
Server 1 Rack
Server 2 Rack
Server 3 Rack
Server 3 Rack
Server 1 Rack
Light ADC
Power Supply
Purity Monitor
Platform
2x2 Private
(10Gb)
Light ADC Rack
Uplinks
Server 1

## Slide 12: Tasks
Phase 1
  Limited AC power – Network rack and Server 1 rack
  In the short term install the router in the network rack and the 1Gb switch in the Server 1 rack
  New Minerva DAQ servers in the Server 1 rack
pORC for each rack
  Partial Operational Readiness Clearance (for one rack)
  Network
  Server 1 (updated)
I'm working with Linda on the rack protection and UPS for the network rack.
  In the short term we can connect the network switches directly to the duplex outlets in the wire way to get the network equipment installation started.
Develop a plan to install the new Minerva DAQ servers in the Server 1 rack while keeping the Minerva readout working.
  New servers will have a different operating system.
  Phased approach?

## Slide 13: Linux Server Purchase Goals
Support the software used at Bern for module testing
  High disk write rates during testing light readout
Modernize Minerva readout servers
Computing for underground operations
Eventually support DUNEDAQ but not immediately
Some servers not included locally
  Network file system servers
  Database servers
  Use NFS and DB from Fermilab central services

## Slide 14: 2x2 DAQ Server
CPU = AMD, mid-range, single socket, 32 cores
RAM = 128GB
Mirrored system disks
~20TB Hardware RAID10
Quad 10GB copper
Dual 10GB SFP+ - for light readout
Fully unlocked IPMI features
5 year warranty
Dual power supplies
Works with latest version of Fermi Linux
Count = 5
  4 2x2 DAQ
  1 Bern slow controls
Test all 4 modules at the same time

## Slide 15: Minerva DAQ Server
CPU = mid-range, single socket, 16 cores
RAM = 64GB
Mirrored system disks
~20TB Hardware RAID 10
Quad 10GB copper
PCI 32 bit 33 MHz for CAEN A2818 card (5V or 3.3V)
  https://www.caen.it/products/a2818/
  Mechanical – half size form factor, 106.65 mm x 167.65 mm (HxL)
Serial port
Fully unlocked IPMI features
5 year warranty
Dual power supplies
Works with latest version of Fermi Linux
Count = 3
  1 DAQ
  1 Nearline
  1 DAQ/nearline spare

## Slide 16: Operations Server
CPU = AMD, mid-range, single socket, 16 cores
RAM = 64 GB
Mirrored system disks
Quad 10GB copper
Fully unlocked IPMI features
5 year warranty
Dual power supplies
Works with latest version of Fermi Linux
Count = 4
  2 gateways
  2 operations and ignition

## Slide 17: Space In HV Filter / Light VGA rack
This rack is on the platform
Distance from the platform surface to the top of the cryostat is ~13 inches (see picture in next slide)
Front of the rack faces the cryostat to minimize cable distances
  I don’t remember which cables
What is the distance from the cryostat to the front of the rack in a birds eye view?
Looks like the space for a 48-port network switch in this rack falls below the level of the cryostat top and will not be accessible
  1U for switch
  1U for cable management
Reviewed the situation with Jack and Tom last Friday at LArTF
Can the rack be supported above the platform with a riser?
  Stability
  Interference with crane
  Interference with ???

## Slide 18: Distance from Platform to Cryostat Top = 13 inches