## Slide 1
FAST / IOTA
Quiet week, not many beam requests (CLARA done, need kicker)
Back-to-back Laser Lab HVAC trips on Tuesday & Wednesday (see: 243144, 243239)
  Thanks to MCR for spotting those overnight; We’re able to recover quickly
  Service contractor came out Wed. to investigate, back-flushed ICW, and did June PM
  Running well now. Head pressure down to 240psi (trips @ 405psi)
SETI experiment ran smoothly Tuesday (See: 243201) – A. Romanov
  Single-Electron Tracking in IOTA
IOTA cable pull stalled due to new oversight; awaiting feedback from contractors
  Top priority – required for completion of Run 4
  IOTA kicker cable replacement , IOTA150-NIO, IOTA150-NIOLD
Down today:
  Cryo expander repair & refrigeration condensation mitigation
  RF Group doing PM on CC1 & CC2 HLRF modulators
  ICW Adams Strainer is clogged. ISD to clean and do PM today and tomorrow
Monday:
    Cryo Wet Engine repair may be extended
    Recovery from Adams Strainer cleaning (Kinney, Laser Lab)
Contact FAST RunCo (J. Santucci, x4996) with any beam or access requests