## Slide 2: Methods and results of heat load measurements (static/dynamic), valid for test stands cryomodules installed in the linac at ESS CM Heat Load Measurements at ESS
PRESENTED BY <NUNO ELIAS>

## Slide 3: Agenda
Static Heat Loads
- Flowmeter (evaporated mass flow)
- Flowmeter (nominal mass flow)
- Flowmeter + 2_point enthalpic difference
- Level Decrease (equivalent evaporated mass)
- Pressure Increase (accrued energy)
Dynamic Heat Loads
- Heater Compensation

## Slide 4: ESS Elliptical Cryomodule at TS2(simple)
The level of the helium bath is measured by two redundant level gauges, LT-01 and LT-02, and it is controlled by regulating the JT valve (CV-01) opening. The typical operating level is 90 %±5 % with liquid on the diphasic line.
The pressure of the saturated helium bath is measured by PT-04 sensor and maintained stable by controlling the VLP return valve (CV-04) placed downstream of the HX.
The flow returned to the TICP is measured after the 2 K pumps by the flowmeters FT-20 and FT-21.
A fraction of the HP helium supply flow is used to cool the power couplers double wall (23 mg/s per coupler), limiting heat loads by conduction from the external vessel parts through the power coupler structure into the cavities.
Sub-headline to strengthen the headline above

## Slide 5: Static Heat Loads (1)
1) Flowmeter method (Evaporated flow):
  - CV01 closed - CV04 opened (pressure regulation)
Constraints :
- Flowmeter accuracy/stability
- Pressure stability/accuracy, level stability
- Transients associated with closing CV01 (bath pressure regulation, uncontrolled pressure between CV04 and cryoplant)
- CV01 Seat leak tightness
Evaporated mass flow

## Slide 6: Static Heat Loads (2)
2) Flowmeter method (Steady State):
- CV01 opened (level regulation) - CV04 opened (pressure regulation)
Constraints :
- Flowmeter accuracy, stability
- pressure stability/accuracy, level stability
- Measuremement accuracy of Thermodynamic properties based of pressure and temperature at Jti
Nominal Flow (steady state)

## Slide 7: Static Heat Loads (3)
3) Flowmeter, Enthalpic difference (Steady State):
- CV01 opened (level regulation); - CV04 opened (pressure regulation)
Constraints :
- Flowmeter accuracy/stability
- Pressure stability/accuracy, level stability
- Measuremement accuracy of Thermodynamic properties based of pressure and temperature
Flowmeter + Enthalpic difference (circuit)

## Slide 8: Static Heat Loads (3)
Flowmeter + Enthalpic difference (circuit)
EH= 12.8 W
- Bath T discrepancy - Redundant sensors discrepancy - JT efficiency (liquid/vapor fraction) - HX heat balance - Heat Loads (syst T errors)

## Slide 9: Static Heat Loads (3)
Flowmeter + Enthalpic difference (circuit)
EH= 24.9 W
- Bath T discrepancy - Redundant sensors discrepancy - JT efficiency (liquid/vapor fraction) - HX heat balance - Heat Loads (syst T errors)

## Slide 10: Static Heat Loads (4)
4) Level decrease equivalent mass:
- CV01 closed; - CV04 opened (pressure regulation);
      With stable pressure:
Constraints:
- Level meter accuracy
- Pressure stability/accuracy
- Manufacturing quality ~ Geometrical model
Evaporated mass (level) over time

## Slide 11: Static Heat Loads (4)
4) Level decrease equivalent mass:
- CV01 closed; - CV04 opened (pressure regulation);
      With stable pressure:
Constraints:
- Level meter accuracy
- Pressure stability/accuracy
- Manufacturing quality ~ Geometrical model
Evaporated mass (level) over time

## Slide 12: Static Heat Loads (4)
4) Level decrease equivalent mass:
- CV01 closed; - CV04 opened (pressure regulation);
      With stable pressure:
Constraints:
- Level meter accuracy
- Pressure stability/accuracy
- Manufacturing quality ~ Geometrical model
Evaporated mass (level) over time

## Slide 13: Static Heat Loads (4)
4) Level decrease equivalent mass:
- CV01 closed; - CV04 opened (pressure regulation);
      With stable pressure:
Constraints:
- Level meter accuracy
- Pressure stability/accuracy
- Manufacturing quality ~ Geometrical model
Evaporated mass (level) over time
Flowmeter
LD equiv. mass

## Slide 14: Static Heat Loads (4)
5) Pressure increase (accrued energy):
- CV01 closed; - CV04 closed;
Constraints:
- Pressure accuracy
- Level meter accuracy
- Manufacturing quality ~ Geometrical model
- CV01/CV04 Seat leak tightness
Accrued energy of system over time

## Slide 15: Static Heat Loads (4)
5) Pressure increase (accrued energy):
- CV01 closed; - CV04 closed;
Constraints:
- Pressure accuracy
- Level meter accuracy
- Manufacturing quality ~ Geometrical model
- CV01/CV04 Seat leak tightness
Accrued energy of system over time
#CM32

## Slide 16: Static Heat Loads (summary)
#CM07
At ESS we use a diversity of methods to calculate the SHL. This allows us to: -> cross-check the results against each other. -> characterize systematic errors of instrumentation -> characterize (up to some extent) the sources of the heat loads. -> better understand the behaviour of the system.

## Slide 17: Dynamic Heat Loads (1)
6) DHL Heater Compensation (Steady State)
- Heaters (on level regulation) - CV01 opened: fixed opening - CV04 opened (on pressure regulation)
Constraints:
- CV01 stability
- DHL stability
- Heater dissipated power accuracy
- Heater level regualtion stability
Compensation of DHL with cavity heaters

## Slide 18: Dynamic Heat Loads (1)
6) DHL Heater Compensation (Steady State)
- Heaters (on level regulation) - CV01 opened: fixed opening - CV04 opened (on pressure regulation)
Constraints:
- CV01 stability
- DHL stability
- Heater dissipated power accuracy
- Heater level regualtion stability
Compensation of DHL with cavity heaters

## Slide 19: Dynamic Heat Loads (1)
6) DHL Heater Compensation (Steady State)
- Heaters (on level regulation) - CV01 opened: fixed opening - CV04 opened (on pressure regulation)
Constraints:
- CV01 stability
- DHL stability
- Heater dissipated power accuracy
- Heater level regualtion stability
Compensation of DHL with cavity heaters
#CM33

## Slide 20: Error quantification ≈ @SHL=20W
SHL:
Flowmeter : Evaporated Flow - 1g/s≈23W);
Flowmeter : Nominal Flow (JT) - 1g/s≈23W); (0.1K ≈2W) ; (1mbar ≈0.1W);
Flowmeter + 2_point enthalpic difference - (1g/s≈23W); (0.1K ≈2W) ; (0.1K ≈3W) ; (0.1bar ≈1W); (0.1K ≈1W); (1mbar ≈0.1W);
Level Decrease (equivalent evaporated mass) - (1%≈1-2W)
Pressure increase (system accrued energy) - (1%≈0.3W); (2mbar ≈ 1W)
DHL
Heater Compensation
      - Heater dissipated power accuracy 1W = 1W
Sources of errors

## Slide 21: Summary of measured heat loads
Static
Dynamic
Total

## Slide 22: Instrumentation and Acquisition
Flowmeters:
- Honeywell QA/QAE Quantometer.
- Weber Vent-captor 3205.30
Sub-headline to strengthen the headline above
Calorimetric principle
Turbine gas meter
Pressure sensors:
- Honeywell STJE.
Pressure conditioning:
- HBM ClipX signal conditioner.
Temperature sensors:
- CernoX
Temperature conditioning:
- Lakeshore - CABTR
Level sensors:
- Cryomagnetics
Level conditioning:
- Cryomagnetics

## Slide 23: Presentation End
Reference: