## Slide 1
Heat Load Measurements at LCLS-II
Lisa Zacarias, SRF Engineer, SC Linac Physics
Presented to the TESLA Technology Collaboration (TTC) on Dec 6, 2023

## Slide 2: Outline
Static Heat Load Measurements
Dynamic Heat Load Measurements
Verifying Linearity
Dissipated Power from Rate of Helium Evaporation
Results
Background
Calibrations
RF Measurements
Single Cavity Extraction
Results

## Slide 3: Static Heat Load Measurements
1

## Slide 4: Verifying Linearity
Set electric heater power to fixed value
Close JT valve to prevent filling
Record averaged rate of liquid level drop
Decrease heater power from 80 W to 0 W in steps of 20 W
Method
Chart: W Vs dL/dt
| 80 | 60 | 40 | 20 | 0
dl/dt | 31 | 23.7 | 16.4 | 9.2 | 1.5
Heater Power | dL/dt (%/hr)
80 W | 31.0
60 W | 23.7
40 W | 16.4
20 W | 9.2
0 W | 1.5
Notes: Average DS and US dLL/dt

## Slide 5: Dissipated Power from Rate of Helium Evaporation
Liquid helium density at 2 K: 0.146
Liquid helium surface area in 2-phase pipe: 10150
1% liquid level change: 3 vertical mm
Mass of 3 vertical mm of liquid helium:
Mass
Latent heat: 23 J/g
Rate of change of mass given r [%/s]: 446r g/s
Power from helium evaporation given r [%/s]: 10225r W
Power
Notes: For CM static heat load the JT valve was closed. So the latent heat of 23 J/g works fine for converting g/s to W.
If the JT valve is open, the conversion factor from g/s to Watts should consider the effect of flash (vapor production downstream of the valve)

## Slide 6: Results
 | EXPECTED CM STATIC | OBSERVED CM STATIC (Initial) | OBSERVED CM STATIC (with Additional Pump)
LO-L2 | 9 W / CM  150 W | 9 W / CM  150 W | 9 W / CM  150 W
L3-UPSTREAM | 9 W / CM  90 W | 47 W / CM  470 W | 17 W / CM  170 W
L3-DOWNSTREAM | 9 W / CM  90 W | 16 W / CM  160 W | 16 W / CM  160 W
TOTAL CM STATIC | 330 W | 800 W | 500 W
Notes: Some CMs had leaky CD valves, which prevented measurement. Expected error ~10%

## Slide 7: Dynamic Heat Load Measurements
2

## Slide 8: Background
Cryomodules built without mass flow meters
Cryomodule helium pressure cannot be isolated (shared cryo piping)
Cavities too strongly coupled to use
  +
Joule-Thomson (JT) valve regulates downstream liquid level
Constant heat load
  Rate of refill = rate of evaporation
  JT valve reaches steady position
Locking JT valve at steady position and changing heat load allows liquid level to change
Why not use existing methods?
Premise

## Slide 9: Calibrations
Measurement heat loads applied on top of baseline 48 W
Linear regression “calibration curve” represents
Y intercept subtracted out as heat load correction
Method
Single cavity heat loads cost time and accuracy
Now measure full cryomodule instead of single cavities
Results
Notes: Low heat load calibrations took a minimum of 5 hours and had corrections as high as 50 W

## Slide 10: Calibrations
Measurement heat loads applied on top of baseline 48 W
Linear regression “calibration curve” represents
Y intercept subtracted out as heat load correction
Method
Single cavity heat loads cost time and accuracy
Now measure full cryomodule instead of single cavities
Results

## Slide 11: Calibrations
Measurement heat loads applied on top of baseline 48 W
Linear regression “calibration curve” represents
Y intercept subtracted out as heat load correction
Method
Single cavity heat loads cost time and accuracy
Now measure full cryomodule instead of single cavities
Results
Notes: Higher heat loads allow for full calibration in as little as an hour with corrections as small as 10^-2 W

## Slide 12: RF Measurements
=
Effective Q
Calibration used significantly impacted measured heat load
Introduced secondary 80 W heater measurement to account for drift
Drift
Notes: Multi cavity measurement required new definition

## Slide 13: Single Cavity Extraction
Heat load with all cavities except cavity i on
Heat load from each cavity alone
Cavity on/off status during measurement
Very time intensive, used as needed
Cavities dissipating < 4 W fall within noise
  Very large error bars
Cavity | Measured (W) | Extracted P (W) | (MV) | 
2 | 52.5 | 11.6 | 16.6 | 2.4e10
3 | 51.2 | 12.9 | 16.6 | 2.1e10
4 | 53.1 | 11.0 | 16.6 | 2.5e10
5 | 61.3 | 2.8 | 10.3 | 3.7e10
6 | 53.1 | 11.0 | 16.6 | 2.5e10
7 | 61.5 | 2.6 | 16.6 | 1.1e11
8 | 51.9 | 12.2 | 15.6 | 2e10
Cavity |  | Extracted P (W) |  | 
2 | 52.5 | 11.6 | 16.6 | 2.4e10
3 | 51.2 | 12.9 | 16.6 | 2.1e10
4 | 53.1 | 11.0 | 16.6 | 2.5e10
5 | 61.3 | 2.8 | 10.3 | 3.7e10
6 | 53.1 | 11.0 | 16.6 | 2.5e10
7 | 61.5 | 2.6 | 16.6 | 1.1e11
8 | 51.9 | 12.2 | 15.6 | 2e10

## Slide 14: Results
Average machine of 2.8e10 exceeded spec (2.7e10)
Cryomodules degaussed pre-commissioning had highest in first round of measurements
Cryomodules degaussed during downtime saw drastic improvement
Degaussing
PPS error led to sudden revocation of all RF permits
  Dropped from 3.5 GV to 0
Cryoplant did not trip
  Heaters able to use calculated to compensate
Stress Test
Cryomodule | Before Degauss | After Degauss | Savings at 16 MV/m
18 | 1.3e10 | 3.4e10 | 104 W
27 | 1.0e10 | 2.6e10 | 134 W
Cryomodule |  |  | 
18 | 1.3e10 | 3.4e10 | 104 W
27 | 1.0e10 | 2.6e10 | 134 W
Notes: Validation of benefits of degaussing strengthened case for it being standard part of CM installation
Almost fully automated
15-20% error

## Slide 15: Final Thoughts
Liquid level-based measurements have proven to be robust enough for standard accelerator operation
  Reliable static measurements led to an improvement of 300 W
  Reliable dynamic measurements validated the use of degaussing in cryomodule installation
Main takeaways
Dynamic heat load measurement details in SRF 23 proceedings
  https://accelconf.web.cern.ch/srf2023/papers/mopmb090.pdf
Extra Resources
Jlab team including but not limited to E. Daly, M. Drury, D. Savransky, J. Kent for initial idea and testing
SLAC cryo group for measurement support; V. Ravindranath, E. Fauve, and A. Apte specifically for static heat load measurement details
SLAC SRF team and operations for assistance in development and data gathering
(Incomplete) Acknowledgements