## Slide 1: Mechanical

## Slide 2: Mechanical – Scope Summary
Provide 5,000-ton Chilled Water Plant to support PIP-II and provide space for future expansion with N+1 redundancy on all major equipment (chillers, cooling towers, pumps)
Provide adjustments to LCW systems (capacities and water quality) to meet updated program requirements
Provide equipment for partial decarbonization of the Heating Hot Water (HHW) plant
Provide space allocation for equipment to fully decarbonize the HHW plant in future phase
Notes: Gordon

## Slide 3: Trend and Future Load Review Summary
7/3/23
Following the discussion between Arup and Fermilab on 6/1/23 and follow up email from JH 7/3/23, the following table summarizes the existing load trends and future loads to be accommodated by the CUB. Proposed capacity of the future CUB chilled water plant is 5,000 tons. PIP-II future loads total 1500 tons (between comfort and process).
Load | Tonnage
Existing buildings (peak comfort + process + LCW 55) | 2,050
Future- IERC Building (Comfort CHW) | 420
Future - PIP-II Linac Gallery (Comfort CHW)* | 350
Future - PIP-II Utility Plant (Process CHW)* | 1,150
Diversity assumed for Future Loads | 90%
Total | 3,778

## Slide 4: 100% PD Mechanical Drawings

## Slide 13: Mechanical – Next Steps
-Development of CD3A Long Lead Items Package
-Development of campus distribution pump pressure drop models
-Fermilab input on connected loads
-Fermilab confirmation of existing distribution piping sizes
-LiDAR scanning of existing plant
Notes: Gordon

## Slide 14: Mechanical – CD3A Long Lead Items
  Chiller
            Magnetic Bearing
            Traditional Oil Bearing
      Cooling Tower
      Electric Boiler
Notes: Gordon

## Slide 15: Chiller
Magnetic Bearing Options
Vendor | Model | Full Load Efficiency [kW/Ton.R] | NPLV.IP [kW/Ton.R] | Refrigerant | Lead Time (Weeks) | Compressors Quantity | Evap PD (ft hd) | Cond PD (ft hd) | Evap min flow
Smardt | WE500.4X.F2BSNB.F2CCNB.TS0 | 0.5832 | 0.3505 | R-513A | 30-34 | 4 | 11.67 | 15.5 | 995
York | YZ-MA129BV120P128HA | 0.6198 | 0.387 | R-1233zd | 22.5 | 1 | 16.1 | 21.9 | 1565
Daikin | WME106CDCSNA | 0.6144 | 0.3727 | R-513A | 33-34 | 2 | 28.7 | 19.6 | 841

## Slide 16: Chiller
Non-Magnetic Bearing Options
Vendor | Model | Full Load Efficiency [kW/Ton.R] | NPLV.IP [kW/Ton.R] | Refrigerant | Lead Time (Weeks) | Extented Warranty Period | Evap PD (ft hd) | Cond PD (ft hd) | Evap min flow
Trane | CVHF | 0.5636 | 0.3824 | R-514A | 30 | Up to 10 years. | 15.2 | 14.2 | 1121
York | YKOKOLK2-FAHS | 0.6098 | 0.368 | R-513A | 22.5 | Up to 10 years. | 21.1 | 22 | -

## Slide 17: Cooling Tower
Manufacturer | BAC | Marley | Marley
Model | S3E-1424-13T |  | NC8413
Capacity [USGPM] | 3750 |  | 
Water Temp [F] | 95/85 |  | 
Stainless Steel Component | Basins |  | 
Lead Time (Weeks) | 15 |  | 
Manufacturer | BAC | Marley | Marley
Model | S15E-1218-11KN |  | 
Capacity [USGPM] | 5100 |  | 
Water Temp [F] | 95/85 |  | 
Stainless Steel Component | Basins |  | 
Lead Time (Weeks) | 15 |  | 

## Slide 18: Electric Boiler
Manufacturer | Precision Boilers | Cemline | Cleaver-Brooks
Model | HW30D-1200D | VB750FTB1260 | WB-243
Capacity [MBTH] | 4094 | 4098 | 4094
Water Temp [F] | 185/200 |  | 
Lead Time [Weeks] | 16-18 | 12-14 | 26
Extented Warranty Period | Pressure vessel 5 years | N/A | Pressure vessel 5 years