## Slide 1: Architectural

## Slide 4
SITE PLAN

## Slide 5
GROUND FLOOR PLAN

## Slide 6
MEZZANINE PLAN

## Slide 9: Exterior Development
Meet value engineering goals
Find a cost-effective, no or low maintenance solution for the existing exterior
Uphold Fermilab’s legacy of distinctive and innovative buildings
Place the CUB chiller operations on display
Support sustainable building strategies
Comply or exceed thermal performance requirements of the IECC

## Slide 10: Value Engineering
Reduce the amount of glazed curtainwall and replace it with less expensive wall assembly
Reduce the amount of screen wall above the roof at the new addition and at the existing lower roof
Replace the screen wall material with a less expensive material
Select a light-weight, low maintenance exterior material that could be direct attached to the existing structured metal panels

## Slide 11: Exterior Materials
Glass Curtain Wall with Insulated Glazing Units
Structured Polycarbonate Panels
Corrugated Fiber Reinforced Polymer (FRP) Siding
Insulated Metal Panels
Cement Board
EDPM Roofing System

## Slide 13: Glass Curtain Wall with Insulated Glazing Units
Insulated Glazing Unit (IGU):
  ¼-inch clear glass (inner light)
  ½-inch air space
  ¼-inch clear glass with low-e coating (outer light)
Winter U-Value: 0.28
Shading Heat Gain Coefficient (SHGC): 0.27
Visible Light Transmittance (VLT): 64%
Curtain Wall: Anodized aluminum

## Slide 14: Structured Polycarbonate Panels
Panel Composition:
  0.4-inch clear matte polycarbonate (inner light)
  3.5 inch space filled with insulation
  0.4-inch clear matte polycarbonate (outer light)
Panel Width: 2-feet nominal
Panel Length: Up to 44 feet long
Panel Weight: 2lbs/SF
Winter U-Value: 0.17
Shading Heat Gain Coefficient (SHGC): 0.20
Visible Light Transmittance (VLT): 16%
Frame: Mill finish

## Slide 15: Structured Polycarbonate Panels

## Slide 16: Corrugated FRP Siding
Composition:
  Existing Double Cell Structural Metal Panel
  ½” Expanded Polystyrene Rigid Insulation
  Corrugated FRP Siding
Panel Profile: 2.68 feet x ½ inch wave
Panel Width: 26 inches
Panel Lengths: 8, 10 and 12 feet
Panel Weight: 0.25 lbs/SF
Color: White

## Slide 17: Corrugated FRP Siding

## Slide 18: Future Steps
Exterior Systems Mock-Ups
  Timing
  Location
Re-examine Roof Slope / Structure