## Slide 1
Maddie Schoell
DOE O 420.2D Assist Visit
September 26-27, 2023
Establishing New Credited Controls

## Slide 2: Outline
ODH Safety Systems
Radiation Detectors
Fluorinert

## Slide 3: ODH Safety Systems
ODH Safety Systems currently exist and are very robust
  Established via FESHM
  Cryo. Engineer review of system to determine ODH Classification (based on quantitative risk assessment)
    Determines components required to maintain classification
    Prescribes surveillance requirements
    Prescribes actions to be taken in the event of component failure
  Established response to ODH Alarms, includes Fire Department/Security, Cryo Coordinator/Facility Manager, and AD Main Control Room (optional)

## Slide 4: ODH Safety Systems
FSO Comment Resolution form excerpt: “Since ODH is not a SIH (in accordance with DOE-HDBK-1163-2020) then this ASE must develop credited controls that will address the ODH concerns with applicable accelerator facilities.”
Response – ODH Safety System components that are required to maintain the posted ODH Classification within an interlocked and/or posted Exclusion Area will be identified as Credited Controls and summarized in the ASE
  Only ODH Safety Systems within Exclusion Areas (interlocked enclosures) are included. Similar systems in other areas are not included.
  If multiple area oxygen monitors are in place, but not all of them are required to be operational to maintain the ODH Classification, not all area oxygen monitors are considered Credited Controls

## Slide 5: ODH Safety Systems
Comments from ARR
  Response to Charge Question
    The Assessment Team judges that the Lab used an appropriate approach for instituting credited controls for ODH components and exclusions areas.
    Training for personnel working in each ODH classification area is judged to be appropriate.
    The concept of when ODH systems must function should be evaluated to ensure that the process provides protection and does not create compliance traps.
    Labeling of ODH credited controls should be consistent throughout the Fermilab site.
  Other comments
    The applicability of ODH credited controls beyond exclusion areas should be evaluated and clarified in the SAD.
Next Steps
  Established Credited Controls for existing systems (i.e., training, labeling)

## Slide 6: Radiation Detectors
Currently implement radiation detectors into Radiation Safety Interlock System (RSIS)
  The RSIS is the Credited Control, specific/individual radiation detectors are not
FSO Comment Resolution form excerpt: “Radiation detectors linked to the RSIS are required in the Shielding Assessment. These are not discussed in the ASE. Are the radiation area detectors/monitors a Credited Control?”
Response – Fermilab will incorporate interlocked radiation detectors as required inputs for the RSIS, and list detectors in the ASE.

## Slide 7: Radiation Detectors
Comments from the ARR
  Other Comments
    Some credited control sections in the ASE define the components that are required to be present. These lists are better placed in the SAD.
Next Steps
  Finalizing agreement between Lab and FSO on which interlocked detectors are Credited Controls and which may be Defense-in-Depth/ALARA
  Finalizing agreement between Lab and FSO on the appropriate place (SAD or ASE) to list Credited Control radiation monitors
  Finalize agreement between Lab and FSO on what constitutes and ASE violation (i.e., if it moves 6in)

## Slide 8: Fluorinert
Through other discussion for future work, discovered that byproducts of fluorinert are created when fluorinert is in a particle beam
Fluorinert currently in use in operational segment of the Fermilab Main Accelerator
  Existing filtration system to filter byproducts
  Commercial system, information limited from manufacturer
    Filter efficiency is unknown
Next Steps
  Clarify what parts of the system are the Credited Control, establish surveillance requirements, labeling requirements, etc.
  Establish procedures & training for personnel working on system

## Slide 9: Questions?