## Slide 1
Geoff Savage
06 November 2023
ArgonCube 2x2 Demonstrator Installation meeting
2x2 Network and Computing Status

## Slide 2: Cabling (not to scale)
catwalk
Minerva LI
Quiet power
copper from server 1 rack
Power Supply
Detector Power
12-port managed switch
Minerva Readout
Quiet power
no network devices
Cryo Rack
EPP power
Computer
UPS
Network
EPP power
48-port router
SFP+ ports
UPS
Light ADC
Detector Power
12-port managed switch
Purity Monitor
Detector Power
12-port managed switch
Server1
Quiet power
Minerva DAQ servers, gateways
48-port managed switch 1 Gb copper
Server2
Quiet power
AC2x2 DAQ servers
Cryostat
Platform Rack
Detector Power
48-port managed switch
Electrical Requirements:
Fiber separates grounds.
No copper between racks on different power.
MND 102
No Power
Trunk
Fiber
x10 for
light
Fibers from racks go
back to Network Rack.
Within each rack copper
from 12-port switch to
each device.
Server3
Quiet power
AC2x2 DAQ servers
x4 for
light
Light ADC has
independent network.
10Gb copper
1Gb copper
fiber
Key:

## Slide 3: Phased Installation Approach
Installation of some components complete
  Phased approach to installation
  Gives experts time to get infrastructure in place
Network (Fermilab Networking Team)
  Router in network rack – uplink to surface tested
  48-port switch in Server1 rack
Computing (Linux System Administrators)
  Two new Minerva servers in Server1 rack
AC Power – 23 Oct 2023
  Matt verified all power outlets under the catwalk
    Quiet building and EPP
  Linda and Matt agreed that power can be restored to all outlets under the catwalk
  Circuit breakers for all outlets under the catwalk were energized
  Minerva readout resumes

## Slide 4: Moving Toward Operations
Racks – network, server2, server3
  Rack protection installed by Rachel and Grant (electrical techs)
  Pantelis and Akeem installed servers, UPS, and connected computer power cords
pORC
  pORC document prepared by – Pantelis, Akeem, Geoff
    https://docs.dunescience.org/cgi-bin/sso/ShowDocument?docid=29419
  Matt performed the as-built inspection last Friday (02 Nov)
Network cabling by Fermilab network infrastructure team
  Started last Friday (02 Nov), continuing today (06 Nov)
  Copper from network and server1 rack to server1,2,3 racks.
  Fiber trunks from network to light adc rack
  Fiber from network rack to server2 rack for light adc network to servers
  Switches in electronics racks – light adc, hv filter, power supply
  Network connection to impedance monitor (gizmo)

## Slide 5: Remaining Tasks
Submit pORC request
  Power to Network, Server2, and Server3 racks
  No networking on detector low-noise power until pORCs for electronics racks are complete
Complete network cabling
Transition all networking to the new equipment
  Not enough 1Gb copper ports to support all new and old servers
  Develop a transition plan
Install operating system (AL9) on new servers – Sys Admins
  Register servers for networking
  Install OS
Configure for operations – vnc, accounts, db, …