## Slide 1
Marty Murphy
Presentation to ES&H RP Group
15 Dec. 2023
0900 AD Scheduling Meeting

## Slide 2: Last Week This Week
Friday – Accesses to remove remaining equipment from tunnel.
Friday - PM: MI-10 and MI2—62 secured.
Monday – Wednesday cleared up the following hurdles:
  Mon. – Completed all work landing of LAM61 power leads onto the PS.
  Mon. – Finalized approvals of the KRSS and associated LOTO procedures.
  Mon./Tue. – Ops subset or trained
  Mon./Tue. – Various small issues discovered and addressed.
  Tue. – Final approval for work on OFF-Hours Work Package approval of KRSS LOTO as requested.
  Tue. - Final approvals for MI ramping.
  Tue.– KRSS switched on by ISD & AD/Ops
  Closed 17/18 VCBs. MI40U VCB won’t close. Basic interventions were unsuccessful it remained off until Wednesday AM. There was an issue at MI20Q as well, but it didn’t affect closing the VCB.

## Slide 3: Last Week This Week
Wednesday – VCB issue at 40U and other problems 20Q PS issues were resolved, and an 8-GeV DC ramp was established and held until Thursday morning.
Thursday – 120 GeV ramp established and preliminary views of Q319 look good. More measurements are needed.
Bend bus regulation error issues are holding off ramp; current suspect is the MI60N current transductor has failed and is affecting regulation. There is a concern about the effect this will have on the harmonic filter. PESD (formerly known as twitter EES) is investigating.
Plan to keep VCBs closed all weekend, but not ramp. Ramp studies will continue Monday.
MI60 Cavity LCW mixing valve is not working; experts are investigating. This does not affect ramp studies.

## Slide 4: Current Status
MI PS on with 8-GeV DC ramp.
PESD is investing ramp regulation issues.
Will not ramp over weekend (leaving open the possibility of ramping on Sunday).
Work continues on SAD/ASE/MCI for 8-GeV and Main Injector enclosures.
Remaining RF work in the tunnel is on hold while we work toward ramping the MI.
LCW conductivity is now around 17 MW
Plan for Friday & Next Week
Finish MI QPS temperature & Q319 bus video measurements early next week. Once those are complete:
Put machines into standby.
  Turn off LCW pumps, but maintain pond pumps in 10 HP mode for winter.
  Switch off at KRSS and resume controlled access to complete remaining jobs until the start of the holiday period.
Remaining Jobs:
  MIRF04 still needs to be tested in situ. This will likely happen after holidays as there is still work to do on the cavity.
  Fix Cavity LCW mixing valve.