## Slide 1
FAST / IOTA Shutdown 2023-2024
Enclosure STATUS: ODH-0 & Supervised Access
ES&H: -South gate of cave. LL OSC Intlks done
IPI: -Cable pull ongoing (2 wks left)(Heliax, VAC)
  -Girders set & mounted. Stands started
  -RFQ rough™ position (on hold)
Cryo: -Working on cryo system: repairs, testing, LN2 #45 (@5K Q3)
ISD: -Lights, “Everything OK alarm”, ICW (Q2), ESB HVAC, -fdr #35 HV PM (May 2024)
Water: -GN2 Back-up system
Contact FAST RunCo with any work or access requests
    There are a lot of jobs going on

## Slide 2: ISD/CFM Report on NML Status
HiBay LEDs is Procurement™ to issue PO (materials are onsite)
Upgrade LED jobs (Exterior and Non-HiBay Interior) RFQ to Contractors
Some lights and E-Lights have been replaced™ or scheduled (Trey)
Emergency Generator:
  Block heater was replaced™ with OEM part on 11/22/2023.
  It isn’t heating “enough”. The “pre-alarm” is alarming. It is hot, but not as hot as expected. Coolant is at 54 degC.
  The generator will start without issue
  New heater repair scheduled™ for Jan 24th
ESB HVAC install – still waiting on contract submittal