## Slide 1
Marty Murphy
05 January 2024
0900 AD Scheduling Meeting

## Slide 2: Last Week This Week
Last Week – Tuesday: MI40 10/40 HP pump tripped and wouldn't restart. 60HP pump wouldn’t start in its place either.
  FESS replaced starter card for both pumps, but that didn’t fix the problem.
  This past Tuesday FESS replaced the entire motor controller for the 10/40 pump. They also accessed the pump vault across from MI40 and found a disconnect damaged from overheating.
  Subsequent investigation shows the wires that run from the 60HP pump starter to the 60HP pump in the vault are burned/damaged and need to be replaced.
  The 10 HP pump system – wires, starter, disconnects, etc. was checked out and restarted without incident.
Ops started the MI Ring LCW system on Wednesday.
RF techs used Wednesday to work on water leaks on RF10 and RF16 cavities.
Ops established a MI ramp on Thursday evening; MI is ramping now.
MI 1.067 second duty cycle PS testing continues this today.

## Slide 3: Current Status
MI ramping.
PESD is investing ramp regulation and other things at 1.067 duty cycle.
Will may ramp over weekend depending on PESD’s (formerly EES) request.
Work continues on SAD/ASE/MCI for 8-GeV and Main Injector enclosures.
Remaining RF work in the tunnel is on hold while we work toward ramping the MI.
LCW conductivity is now around 10 MW
Plan for Friday & Next Week
Finish MI ramping measurements.
Return to controlled access.
Put MI/RR into standby.
Supervised access for SAD/ASE tunnel tours.
Remaining Jobs:
  MIRF04 still needs to be tested in situ.
  MIRF10 & RF16 LCW issues.
  Remove equipment from MI60 MVA.