## Slide 1: Sight Riser Specification-Preliminary

## Slide 2: Cross-section of Primary Beamline

## Slide 3: Cable Tray Sizes and Configuration

## Slide 4: Sight Riser
Sight Riser Fill:
  7.5’ of sand polyethylene mix
    5’ sand + 2.5’ polyethylene
  1’ tall polyethylene cylinder at top of sight riser (inside)
  2” thick steel plate at top of sight riser (with air seal)
Primary Beam Tunnel ceiling

## Slide 5: Sight Riser Details
Thin-walled tube will be 3’ long
There will be a pipe joint 1’ off the ground.
At the joint, there will be a 2” thick steel plate with a 1’ long polyethylene cylinder
Grade
2 inch plate
3 foot
1.0 foot

## Slide 6: Alignment Between Sight Riser and Monument
Required Tolerance=1”

## Slide 7: Detail of Sight Riser On The Surface