## Slide 1: Muon Campus Operation Report
Jim Morgan
Friday 09:00 Operations Meeting
June 14, 2024

## Slide 2: Muon Campus status
Study – Alternative M5 optics
Study – M1-M3 Optics
Resumed running beam last Friday after D:IB issues resolved
  Delivery Ring BPM’s timed in late Friday afternoon and early evening
  Have first turn flash frames since Tuesday, need closed orbit data
Took beam during day shifts to work on Delivery Ring BPM’s
  Improvements made since a year ago, but need to recommission system
  Worked on M39 program issues posting M1 BPM’s with key experts back at lab
Warm power supply panel circuit breakers
  D:Q730 needs larger breaker and wiring, thermally scanning all circuit breakers
  D:V907 has reasonable primary phase currents but has still tripped breaker
Check-out of extraction skew quadrupole power supply
Delivery Ring RF water control valve electronics swapped, now works properly
  Have found that resonance is at higher temperature than expected
  Cooling water temperature excursion this morning due to chiller trip
ESS1 & ESS2 Electrostatic Septa
  ORC got approval from ES&H (Industrial Hygiene) on Monday, signed off Tuesday
  D:ESS1 power supply safety tested, then needed some final work before powering
  Vacuum has been good enough to begin powering ESS1 & ESS2
AP-0 A/C work continues to be stalled (now at 60 weeks)
  Portable A/C unit working well, after rough start

## Slide 3: Delivery Ring RF temperature excursion this morning
Chilled Water return temperature
Heat Exchanger inlet temperature
Skid temperature valve position
RF cavity gap envelope
Chiller trip

## Slide 4: Delivery Ring RF cavity temperature and resonance
Amplifier forward power
Cavity gap envelope
Cavity LCW supply temperature
Skid temperature valve position
Amplifier reverse power

## Slide 5: ESS1 & ESS2 vacuum pump-down

## Slide 6: Upcoming work
Studies priorities
  Finish making Delivery Ring BPM’s work, need closed orbits working
  Smooth closed orbit in Delivery Ring and adjust injection closure
  Continue working on M39 problems with M1 BPM’s not posting to RR to DR view
  When power supply ready, begin conditioning ESS1 & ESS2
  First turn extraction without kicker using quadrupole moves
  Establish resonant extraction when ESS1 & ESS2 are ready after conditioning
  Try to get M4 multiwire profiles with resonantly extracted beam
Other issues
  Delivery Ring 2.5 MHz RF cavity needs to have resonance adjusted
  D:Q730 needs larger breaker and wiring to run at nominal current
  D:V907 occasionally trips breaker though primary current reasonable
  Have several circuit breakers running warm, working to understand why
  D:QT405 power supply voltage maxed out, output tracks line voltage
  Old BR trim power supplies running out, will use those from M2 Line as spares
ESS2
  ESS2 cathode electro-polishing next, choosing vendor
  After cathode polishing is complete, then component assembly into tank
AP-0 A/C work paused while awaiting controls sub-contractor