## Slide 1: Controls for Air and Nitrogen Systems
J. Lewis
Integration Meeting
17 July 2024
v1 – posted DD Month

## Slide 2: Overview
NSCF designing and installing all air and nitrogen handling systems
  Includes cooling of target and absorber piles
  Will use PLCs with HVAC communications standards
    BACnet (ASHRAE 135)
  Includes full suite of software for operations
ISD responsible for comfort systems and infrastructure
  Won’t accept responsibility for process systems for program elements, i.e. Beamline cooling
AD must control Beamline systems and RAP
Hybrid ownership and control

## Slide 3: System Types
All systems are controlled over IP
  Assign to networks based on beam-on control
    Shutdown control in attached table is for purposes of maintenance, not day-to-day operation
Need information shared between networks
  Examples:
    AD needs temp of chillers from ISD network
    ISD needs status of DOAS units from AD network
  Require gateway to communicate between networks
Type | Owner | Beam-on Control | Shutdown control | Control Type | Network
NHUs | AD | AD | AD | PLC | AD
Absorber pile AHU | AD | AD | AD | PLC | AD
RAP AHU | ISD | AD | ISD | PLC | AD
Exhaust Fans for enclosures | ISD | AD | ISD | PLC | AD
RAP Exhaust (EE-EF1) | AD | AD | AD | PLC | AD
OPAV DOAS | ISD | AD | ISD | PLC | AD
High-bay AHU | ISD | ISD | ISD | DDC | ISD
RAW, HPS, Controls room cooling | ISD | AD | AD | DDC | AD
Air-cooled chillers | ISD | ISD | ISD | DDC | ISD
Hot and cold water pumps | ISD | ISD | ISD | DDC | ISD
Unit heaters | ISD | ISD | ISD | DDC | ISD
Evaporator System and condensate pumps | AD | AD | AD | PLC | AD

## Slide 4: System Maps
Graphical representation of system types for all three complexes (PB, TC, AC)
  See DocDB-31413
    Diagrams currently from 60%
    To be updated soon
    Spreadsheet is up to date
Key
  PLC, AD owned
  PLC, ISD owned
  DDC, ISD owned

## Slide 5: System Map: TC

## Slide 6: System Map: AC

## Slide 7: Networking
All network switches to be provided by lab to contractor
  AD for ACNET
    Connect beamline HVAC systems on isolated VLAN for commissioning
      Per Tim Zingleman
  CD site network for ISD
    They also have a secure VLAN for building automation systems
  Need port counts for all facilities
    Complete table below!

## Slide 8: Network Diagram
Gateway
Dedicated ISD vlan on site network
Dedicated ACNET vlan on isolated AD network

## Slide 9: Beam Permit
One permit signal for each PLC-based subsystem
  Example: TC-NHU-1
  Will be logical AND for all alarm tests for that subsystem
Require saving snapshot of all quantities when permit is dropped for a subsystem
Relay contact or TTL signal (TBD)

## Slide 10: Control System Deliverables by NSCF Subcontractor
Complete controls systems using commercial software with a fully implemented Human Machine Interface (HMI)
  Separate systems for PLC vs DDC based
    Readonly access to data from other system via gateway
  Includes servers and workstations
    Question: Where to house servers and gateway?
  Can run on any internet-connected computer
    E.g. laptop
    Subject to network security
  Will include settings of all devices
    NSCF commissioning agent will balance all systems prior to AUP
    Beamline should bring them back to update settings once TSP, horns, and absorber pile are fully installed
  Will include sequences for different operations conditions
    Beam-on, NHU access, bunker nitrogen fill, etc.
Complete listing of all BACnet I/O variables
  Includes settings and alarm levels
  Can integrate with ACNET/ACORN using EPICs interface

## Slide 11: Control System Issues
Standalone system delivered at AUP
  Less than ideal for MCR
  Need to integrate to ACNET?
    At what level?
      Routine monitoring only
      Include all monitoring and control functions
        Can effectively function as an alternative workstation reading or setting values
    Issue for ACORN, Ops?
    I would keep software off LBNF project
What is desired complexity of sequences?
  Include all three complexes in each sequence?
  Need small-group discussion. Volunteers?

## Slide 12: Action Items
Validate equipment control/ownership
Include commissioning agent prior to beam startup
Update network counts
Schedule installation of AD network devices during NSCF construction
Review operations sequences