## Slide 1: Muon Campus Shutdown Report
Jim Morgan
Friday 09:00 Shutdown Meeting
September 13, 2024

## Slide 2: Muon Campus status
Study – Alternative M5 optics
Study – M1-M3 Optics
ESS2 survey of cathode and wire plane at A0 Clean Room
  Second survey required after adjusting cathode supports to reduce warp
D30 downstream mechanical work waiting on key Q205 part (~2 weeks out)
Transport “Y” sump check valve replaced
LCW leak rate greatly reduced after MSD repaired or valved out known leaks
  Largest leaks on sub-header connection and a Delivery Ring sextupole
  Resistivity has been declining, may be time to change DI bottles at CUB
ESS1 & 2 Fluorinert piping installation complete
  Connects future AP-30 cooling skid with surge resistors in the tunnel
Prototype ESS2 will need to be removed from DR prior to running beam
  Related to buyback accounting between Mu2e Project and AD spares funds
  Hope that operational ESS2 will be ready for installation in October
  Will evaluate options if operational ESS2 is delayed significantly
Domestic water leaks near AP-0 adjacent to Transport berm
AP-0 north door replaced
AP-0 A/C work continues to be stalled

## Slide 3: Transport “Y” sump check valve replaced

## Slide 4: Muon LCW make-up rate and decline in resistivity
LCW return pressure
LCW resistivity
LCW make-up

## Slide 5: Delivery Ring extraction region
Delivery Ring
M4 Line
Q205
Extraction Lambertson
Special vacuum pipe
Q205 on support “plate”
Extraction C-Magnet

## Slide 6: Upcoming work
Main worklist items and other upcoming work
  AP-0 Dump system will be drained and water lines blown out
  Install rad hard 8Q24 at Q205, send uninstalled 8Q24 to TD for rad hard water lines
  Q205 vacuum pipe replacement to simplify vacuum connection to ELAM
  Unroll ELAM? (was rolled 24 mr to improve g-2 extraction trajectory)
  Profilometer extraction profile monitor vacuum Tee installed upstream of ELAM
  Several alignment tasks including D30 level run and M4 Final Focus
  M4 Final Focus vacuum installation, A/C dipole installation
  Need to check sizing of all power supply panel breakers, upgrade as necessary
  Repair Kirk Key hardware on disconnects
  Most LCW leaks repaired, but a few left to fix
  Install additional steel shielding above ECMAG
  ESS1 and ESS2 septum stand motion-control improvements
  Hope to finish operational ESS2 and install it in tunnel late in shutdown
  Repair of domestic water break near AP-0 may disturb Transport berm
ESS2 (operational version in A0 Clean Room)
  After survey, vacuum leak check and transport to NWA for high voltage conditioning
AP-0 A/C controls work paused; reason unknown