## Slide 1
Tony Busch/Cons Gattuso
AD Shutdown Coordinator
Planning & Integration Department September 20th
Accelerator
Summer Shutdown

## Slide 2: Critical Path
  Site Power Configuration and Remaining Outage
    Assessments/repairs at both substations are underway
    The goal is to get at least 4 of the 8 main transformers in an Operational State
    We have a plan as to how power and distribute loads between the substations.
      We will need to balance/verify loads between the substations
      Still not clear how much of the complex we will be able to run
      We have an associated risk in running in this mode
    Remaining power outage
      These maintenance Power Outages must occur prior to turning on. (working getting them scheduled)
        Linac L1/L2/L3
        MI Pulse/Conventional power at MI8, MI10, MI20, MI30, MI40
  MI Heat Exchange
    During cleaning process, it was discovered that over the years we have lost thickness due to corrosion.
      We have a vendor coming next week to inspect the heat exchangers and give us a better Idea as to how much material we have left, which will indicate our next course of action.
      To run BNB will need MI LCW flowing ring wide. But not at full capacity.

## Slide 3: Tunnel Clean up
Clorica will begin cleaning of the tunnel spaces next week (Subject to change). Rich White is coordinating/managing this effort.
  Linac: Wed 9/25
  MTA: Thurs 9/26
  Booster: Fri 9/27
  MI12A/B: Mon 9/30
  MI10: Mon 9/30 – Thurs 10/3
  MI20-62: Fri 10/4- Wed 10/9
  F-Sector: Wed 10/9 – Thurs 10/10
  Muon Campus
    Transport Us/Mid/Ds Fri 10/11
    Delivery Ring/Extract/M4 Week of Oct 14th
Rad waste Disposal (generated over the years)
  A4 Service Bldg. (picked up already)
    (6) Rad barrels
  Booster (to be picked up next week)
    (1) 4ft x 4ft x 4ft Container
    (3) Rad barrels
  In the queue, we have waste from MI/NuMI/Muon Campus, etc.)
    ~ 10-15 Barrels
    (6-7) 4ft x 4ft x 4ft Container
    ~ 5-7 Pallets of material
    Maybe more????
  Work on processing other waste stream disposal is underway….

## Slide 4: Moving Towards Beam Operations
Linac
  Complete Secure of Linac the weekend of Sept 28th
    Enclosure will remain Controlled Access
  Complete Safety system interlock testing
    Monday October 1st
  RF Turn on is driven by the following
    Master/Kautz Sub station configuration
    Linac Power outage complete
    DI bottle issue resolved for water skids
Booster
  Recore back to operational key set at the EOB Mon Sept 30th
  Complete Secure of Booster Tuesday evening shift Oct. 1st
  Safety system testing Wednesday October 2nd
BNB (MI12A/B)
  Complete Secure of MI12A/B the October 6th
    Enclosure will remain Controlled Access
  Complete Safety system interlock testing
    Monday October 7th
MI-8
  Driven by Collimator install completion and restore LCW operations

## Slide 5: Reminder
I will be acting ShutCo until 18:00 hrs today….
  Tony resumes his responsibilities..
Any questions?