## Slide 1
Tony Busch
AD Shutdown Coordinator
Planning & Integration Department
Accelerator
Summer Shutdown

## Slide 2
Shutdown 2024 Timeline
Crew Marching orders
Determine Jobs
Plan phase 1: Define schedule
Execute Shutdown
Close out
Plan phase 2: Finalize Schedule
JAN
FEB
MAR
APR
MAY
JUN
JULY
AUG
SEP
OCT
NOV
DEC
Milestone 1
Define Shutdown Coordinators.
Milestone 2
ID Jobs to the 90% level.
Milestone 3
First pass resource level Schedule.
Milestone 4
Milestone 5
Milestone 6
Milestone 7
Second pass resource level Schedule.
Final resource level Schedule.
Start Shutdown.
Complete shutdown.
Milestone 9
Milestone 8
Complete
Startup.
Return HEP
Define Scope
Plan
Execute
HEP
Dec
Execute
Execute Shutdown
LOMO
Shutdown parameters
Original Duration: 10 weeks. LOMO period extended the timeline. We have also had some unforeseen problems come up with Kautz and Master Sub stations along with the Main Injector Heat exchangers.
Beam to BNB 11/1/24

## Slide 3
Plan for restoring substation operations
Phase | # Operating Transformers | Description | Impact | Timeline
1 | MSS: 2 KRS: 2 | Make repairs to Kautz Road Substation, modifications to Master Substation to restore two transformers within each station | Remove single point vulnerability, restore power service to BNB program Restore partial Main Injector operations | ETA: 30 Sep 2024
2 | MSS: 2 KRS: 3 | Make repairs to T81, relocate to Kautz Road Substation | Restore partial Main Injector operations | 6-9 months
3 | MSS: 3 KRS: 4 | Replace suspect bushings on T84 and T87 | Restore full Main Injector operations | 12-28 months
4 | MSS: 4 KRS: 4 | Replace damaged transformer | Restore resiliency within electrical distribution system | 36+ months
Plan for restoring substation operations - overview

## Slide 4: Main Injector heat exchanger inspections
While inspecting the cleaned Main Injector heat exchangers, AD engineer noticed that the interior of the heat exchanger channels are experiencing severe corrosion.
Engineers are working engineering notes to run the heat exchangers as is with precautions.

## Slide 5: Shutdown Progress
Chart: 
 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Planned Work | 1 | 0
100.0%
Planned Work
Chart: 
 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Work Completed | 0.651 | 0.349
65.1%
Work Completed
I anticipate that we will be at ~ 80% of the work completed once
the collimator work and testing is complete.

## Slide 6: Power outage schedule
Chart: Electrical power outages
| % Not Completed | % Complete | % Deferred/Rescheduled
 | 0.45588 | 0.25 | 0.29412

## Slide 7: 8 Gev Collimator
2 Collimators
  825-826 and 827-828
Weight per collimator station: ~175,000 lbs. (88 tons)
Beam direction
Beamtube/ vacuum chamber
Vertical motion controls
Horizontal motion controls
Installation is 50% complete

## Slide 8: Booster Collimator
1 Collimator on 2 stands
Weight ~100,000 lbs.
Beam direction
Vertical motion controls
Installation complete
  Working on controls for motors.

## Slide 9: Main jobs completed
  Dual PA upgrades in Main Injector continue
  Replacement of H202-5 and SWIC in Switchyard.
  Choke repairs in Booster.
  Sump discharge repairs in Main Injector
  Cleaning of all Main Injector heat
  exchangers. Inspections continue.
  Booster collimator installed
  MI 8 collimator continues.

## Slide 10: ISD Shutdown work completed
  Electrical
    Lighting repairs
      Tunnel relamping
      Service Building relamping
    Power panel inspections
      Tunnel and service buildings
    General Electrical repairs
    Upgraded the MI 40 sump controller
  Mechanical
    Sump repairs/replacement
    Generator maintenance

## Slide 11: Summary
Main Injector heat exchanger inspections continue.
KRS work continues. Power outage on 10/16 to normal configuration.
Linac plans to run beam by the end of the week of 10/7.
Booster awaiting shielding assessment.
Beam to BNB 11/1.