## Slide 1: Muon Campus Shutdown Report
Jim Morgan
Friday 09:00 Ops Meeting
November 22, 2024

## Slide 2: Muon Campus status
Study – Alternative M5 optics
Study – M1-M3 Optics
Electrostatic Septum ESS2 installation and new stand check-out for both septa
  Vacuum continues to pump down in ESS region
  Noticed periodic vacuum “burps” on ion pumps and ion gauges
  Clearing electrode power supply work on ESS2
  Motion-control check-out began on ESS1 & ESS2, modifying limit switch brackets
Q205 rad hard quadrupole and modified vacuum pipe installation
  Quadrupole was aligned on Wednesday
  Vacuum connections still need to be made up
  Some discussion about new Q205 pipe geometry and vacuum connections
Domestic water line repair north of AP-0 and over MI-8 Line
  Berm integrity needs to be checked after repairs
Ring, Extraction and M4 Enclosure doors switched back to operational cores
  Shutdown keys no longer work, need to get keys from MCR for access
Muon LCW resistivity continues to be poor
LCW make-up rate increased yesterday, not sure it’s a leak
AP-0 A/C work paused, reasons unclear

## Slide 3: ESS region vacuum pump-down
Ion Pumps
Ion Gauges
Target vacuum for high voltage conditioning

## Slide 4: Periodic vacuum burps in ESS region

## Slide 5: Muon LCW daily make-up volume
LCW return pressure
LCW conductivity
Daily make-up

## Slide 6: Upcoming work
D30 installation work
  ESS area vacuum pump-down continues, trying to understand source of “burps”
  Hope to reach target 1E-8 Torr on ion gauges for high voltage conditioning next week
  Q205 vacuum connections and pump-down
Domestic water line repairs south of AP-0 may have compromised shielding
  Close to Transport berm, need to survey to understand if berm was disturbed
  Excavation for new water line crossed over MI-8 tunnel
Other upcoming work
  Continue ESS1 & ESS2 motion-control check-out and limit switch modifications
  Repair Kirk Key hardware on disconnects, requires more modifications to disconnect
  Replace several power supply circuit breakers and some primary wiring
  Prepare to install Mu2e Extinction Monitor Collimator in Absorber area
  M4 Final Focus vacuum installation, A/C dipole installation
Preparing for beam operation later this month
  Safety system testing
  Final walk-throughs and corrections before powering magnets
  Work towards power supply check-out and preparations for beam
  Concerned that PIP-II construction could impact beam operation in January