## Slide 1: Linac Operations Report
HEP beam for Booster studies/tuning
Bunch Length Detector studies
Beam output: Source: 57.8 mA
TO1IN: 25.5mA
D7TOR: 23.5 mA
Efficiency: 92 %
Tuesday
  Klystron waveguide compressor air dryer leak
    DM attempted to fix, but parts are needed for repair
    Dryer valved out for now, running on backup dryer for now
Thursday
  LRF4 trip during DI bottle change
    RF water skid tripped causing filament to turn off
    Marx PLC required a power cycle
    Station recovered in < 2 hours
  KRF2 Sol #2 PS failed
    PS replaced within the hour