## Slide 1: Muon Campus Shutdown Report
Jim Morgan
Friday 09:00 Ops Meeting
January 17, 2025

## Slide 2: Muon Campus status
Study – Alternative M5 optics
Study – M1-M3 Optics
Power supplies were run for several days with a few lingering issues
  D:IB bi-modal output, apparent controls or reference issue
  D:V907 trips breaker after hours of running
  D:QSS apparent bad klixon was found to be shunt trip, need better digital status
  Pulsed devices checked out
  Pre-Vault and Pre-Target supplies couldn’t be tested with Feeders 94/95 off
  Kicker charging supplies for Mu2e require different TLG timing
  LCW temperature return temperature appeared high, apparent readback problem
Electrostatic Septa conditioning
  Began December 27, nearing completion
Controlled Access period began Wednesday
  Thermal scan of magnets
  Located and addressed two LCW leaks in Delivery Ring
  Safety check of air pressure at Beam Stop locations
  Need to address Beam Valve BV510 not showing “open” status this morning
Recovery from short power outage on Thursday morning
  Muon Feeder 24 now backfed from Main Injector Feeder 53 via connection at AP-0
  Maximum sustained load on Fdr 53 is 6 MW (MI 2.5 MW, Muon 3 MW during ops)
AP-0 A/C work remains paused

## Slide 3: Electrostatic septa conditioning
ESS1 Voltage
ESS1 Spark Counter
ESS2 Spark Counter
ESS2 Voltage
Delivery Ring access
Operational target voltage
Delivery Ring access
Feeder 24 power outage

## Slide 4: Metasys CUB data from Tuesday afternoon

## Slide 5: Muon LCW Acnet temperatures
CUB Return Temperature
CUB Supply Temperature
MC-1 Return Temperature
Delivery Ring Access
MC-1 Supply Temperature
Metasys CUB
Supply Temperature
Metasys CUB
Return Temperature
Metasys CUB
Return Temperature
Metasys CUB
Supply Temperature

## Slide 6: Upcoming work
Minimal remaining tunnel work
  A/C Dipole cable pulls from MC-1 to M4 Enclosure (need Supervised Access on Tue)
  Sump monitors for the Mu2e Detector Hall and Pre-Vault Enclosure
Turn power supplies back on after access and fix ones that are problematic
  Deciding whether to turn on M4 for weekend, or leave off for cable pulls
Apparent high LCW return temperature appears to be bogus readback
Finish ESS High Voltage Conditioning
  ESS2 has reached operational voltage of 85.7 kV, ESS1 is getting close
Finish Critical Device Testing
  Need Beamline Feeders 94/95 to be powered
Preparing for beam operation
  Work towards resolving remaining power supply problems
  Assuming that beam can be delivered from the Recycler
Expect PIP-II BTL construction will prevent Muon Campus beam for 6 weeks
  Starting approximately January 29
Hope to address warm power supply circuit breakers during 6-week pause
  Replace several circuit breakers identified as running warm (especially V907)
  Increase wire size on a few circuits to improve margin