## Slide 1: Muon Campus Shutdown Report
Jim Morgan
Friday 09:00 Ops Meeting
January 31, 2025

## Slide 2: Muon Campus loss of cooling water while powered
Study – Alternative M5 optics
Study – M1-M3 Optics
Loss of LCW flow from CUB early Sunday morning led to magnet damage
  CUB lost power at 02:26, Muon Campus remained powered
  MC-1 fire alarm at 02:42, probably from “Protectowire” in Extraction Enclosure
  Many power supplies continued to run after loss of LCW
  Some power supplies continued to run until tunnel access into DR & Extraction
  Three power supplies in Transport ran 88 min. until turn-off commands were sent
  Many power supplies tripped off, due to magnet temperature or other trip inputs
  Not all power supplies were running, P1, P2, M1, M2 & M5 were off
  Some magnets more vulnerable depending on type and dissipated power
Three MDC dipoles badly damaged from heat, V742, V743 & V906
  Magnet thermal protection (klixons) and wiring checked out okay after incident
  D:V742 and D:V906 power supplies are both Spang supplies
  MDC dipoles have relatively high heat dissipation
Remaining concern over the health of other magnets
  Beginning to test approximately 30 magnets that had high dissipated power and/or a long period without cooling water
  Have performed visual inspection of all magnets that were powered on Sunday
  No obvious signs of heat damage on other magnets
Smell from damaged coils remains in tunnel, sticky layer on nearby objects

## Slide 3: Electrostatic septa conditioning

## Slide 4: Timeline of events and magnet dissipated power
Minutes
Time
Power
Current

## Slide 5: Location of damaged dipoles
V742
V743
V906
Delivery Ring Enclosure
D30 straight section

## Slide 6: MC-1 fire protection Protectowire in Extraction Enclosure
Protectowire
M4 Line
V906
Intake for exhaust fan
on berm north of AP-30
Delivery Ring Enclosure
Extraction Enclosure

## Slide 7: V742 Dipole
Coil damage
Before

## Slide 8: V743 Dipole
Coil damage
Before

## Slide 9: V906 Dipole
Coil damage
Before

## Slide 10: M5 MDC dipoles
M4 Line
M5 Line
H005

## Slide 11: Moving forward
Klixons and magnet coil information
  Klixons open at 80C, TD experts think placement on magnet is correct
  Magnet coils are wrapped with fiberglass tape, impregnated with epoxy
  TD experts say that epoxy will blacken above 250C
  TD experts also said that epoxy must be above 650C to burn
  In my opinion, there is no evidence that there was a fire
  There was lots of smoke and heat however, Protectowire generates alarm at 88C
The (technical) path ahead
  Need to replace three failed dipoles
  Only one true spare, but four suitable MDC dipoles in M5 Line since g-2 has finished
  Three M5 Left Bend dipoles H005, H008 and H011 will replace damaged magnets
  M5 dipoles have special vacuum pipes, MSD has located three standard pipes
  The V906 magnet hanger may need new parts due to the difference in MDC types
Check magnet thermal protection, especially ones with newer power supplies
Did not get beam sign-offs completed prior to Sunday’s incident
PIP-II 6-week pause began earlier this week
Hope to address warm power supply circuit breakers during 6-week pause
  Replace several circuit breakers identified as running warm (especially V907)
  Increase wire size on a few circuits to improve margin