## LCLS-II vols
|  | Updated with LCLS-II pipe inner diameters | TJP | 2014-04-18
| Average module cold length = | 12200 | mm
Location | Number of | State | Temperature | Pressure | Pipe ID | Density | Volume | Mass | Equiv liquid | Number of
| modules |  | (K) | (bar) | (mm) | (kg/m3) | (liters) | (kg) | (4.2 K liters) | Tevatron
Volumes
One helium vessel |  | liquid | 2 | 0.031 |  | 145.7 | 23 | 3.3511 | 26.8088
8 helium vessels | 1 | liquid | 2 | 0.031 |  | 145.7 | 184 | 26.8088 | 214.4704 |  |  | 9
2-phase pipe liquid | 1 | 1/2 dia liquid | 2 | 0.031 | 95 | 145.7 | 43.2162 | 6.2966 | 50.3728 |  |  | 1200
2-phase pipe vapor | 1 | 1/2 dia vapor | 2 | 0.031 | 95 | 1.008 | 43.2162 | 0.043562 | 0.3485 |  |  | 10.8
300 mm pipe vapor | 1 | vapor | 2 | 0.031 | 300 | 1.008 | 861.93 | 0.86883 | 6.9506 |  |  | 125
5 K supply | 1 | supercritical | 5 | 5 | 56.1 | 129 | 30.1408 | 3.8882 | 31.1053 |  |  | 1350
8 K return | 1 | supercritical | 8 | 4 | 69.9 | 30.76 | 46.7933 | 1.4394 | 11.5149
30 K supply | 1 | gas | 30 | 16 | 72 | 24.66 | 49.6472 | 1.2243 | 9.7944
50 K return | 1 | gas | 50 | 14 | 79.4 | 12.97 | 60.3769 | 0.78309 | 6.2647
Warmup line | 1 | vapor | 2 | 0.031 | 38.9 | 145.7 | 14.492 | 2.1115 | 16.8919
TOTALS
One module | 1 | [5 empty] | 1333.8126 | 43.4642 | 347.7135
LCLS-II module total | 37 | [5 empty] | 49351.0665 | 1608.1751 | 12865.4009 | 0.21442 | Tevatron inventories
[9 empty] | 15438.4811 | liquid liters with 20% over factor
[9 empty] | 6.7535 | propane tanks for all the helium
| Volume |  | Equiv liquid
| (liters) |  | (liters)
8 helium vessels | 184 | 13.8% | 214.4704 | 61.68%
2-phase pipe liquid | 43.2162 | 3.24% | 50.3728 | 14.49%
2-phase pipe vapor | 43.2162 | 3.24% | 0.3485 | 0.1002%
300 mm pipe vapor | 861.93 | 64.62% | 6.9506 | 1.999%
5 K supply | 30.1408 | 2.26% | 31.1053 | 8.946%
8 K return | 46.7933 | 3.508% | 11.5149 | 3.312%
40 K supply | 49.6472 | 3.722% | 9.7944 | 2.817%
80 K return | 60.3769 | 4.527% | 6.2647 | 1.802%
Warmup line | 14.492 | 1.087% | 16.8919 | 4.858%
Cryomodule TOTAL | 1333.8126 | 100% | 347.7135 | 100%