## Slide 1: Mu2e Conventional Construction Value Engineering
Lee Hammond
VE Study Coordinator
7/9/2014
U.S. DEPARTMENT OF
ENEGY
Office of
Science

## Slide 2: Value Engineering @ start of Final Design
Workshop was held in 2013 on Feb 14th and 15th
Based on US Army Corp of Engineers Methodology
  20 participants including the major discipline leads from the A&E.
    Also used as an introduction to the A&E team.
  Speculation list contained 62 items; 20 have been accepted.
The project was described by the project technical teams (PM, Accelerator, Solenoids and Muon Beam) and the Conventional Construction design engineers.
The VE process was defined and the charge to the panel was given.
A functional analysis of the experiment along with the physics goals was described by the project’s experimental team.
The speculation session followed. The group was encouraged to make proposals for value engineering ideas, whether they affected budget, schedule, quality or life cycle cost of the project. At this point there are no bad ideas; all are accepted.
The proposals were gathered into a Speculation List and a first cut was made. Accepted proposals were selected for further evaluation.
With the Speculation List organized into engineering disciplines, members of the project team were assigned to develop and lead the further evaluation of the selected proposals.

## Slide 3: Speculation List

## Slide 4: Highest value proposals
Items with major value impact
  Eliminated Kautz Rd bypass
    The building falls squarely on existing Kautz road and could not be moved due to beamline lattice constraints. The Advanced Conceptual Design had the road moved behind the building.
    By eliminating the portion of road between Giese and South Booster Road we saved excavation of the stockpile and gained space for stockpiling of excavated earth from the building foundation.
    Radiation studies have shown that the earth where the road would have been relocated to is needed for shielding.
  Reduced number of stairs tower
    Eliminated the stair from the remote handling Room and replaced with horizontal passage to adjacent stair.
  Increased crane hook height
    By raising the crane hook height (and overhead door) it allows for the solenoids to be delivered on a either a special low boy or special flatbed truck trailer. At this time the trailer type has not been determined.

## Slide 5: Continued VE
On going value added measures subsequent to the VE workshop include:
  Underground FRP pipe changed to epoxy coated/cement lined carbon steel pipe. FRP was deemed a collapse risk especially during possible future excavation.
  Double wall ductwork changed standard galvanized in areas where corrosion risk are considered low.
  ICW vacuum pump cooling changed to chilled water cooling to prolong vacuum pump life.
  Enhanced the outside air supply system by applying a side stream desiccant unit to reduce incoming air dewpoints by 10 degrees F.
  Electrical floor plan layouts were optimized in collaboration with AD personnel.
  Repurposing transformers and switchboards from DZero