## Slide 1: Mu2e CD-2 Life Safety Review
Jim Niehoff
ES&H (Fire Protection) Safety Specialist
7/8/2014
U.S. DEPARTMENT OF
ENEGY
Office of
Science

## Slide 2: Requirements (Objectives)
Provide successful evacuation
Provide effective fire fighting and rescue operation
Limit spread of fire and smoke
  Fire suppression systems
  Fire alarm systems
  Smoke abatement

## Slide 3: Requirements (Determined)
AON’s recommendations are based on codes/orders/standards:
  DOE Order 420.2C Safety of Accelerator Facilities
  IBC (International Building Code)
  IFC (International Fire Code)
  NFPA (National Fire Protection Association)
Aim of Life Safety
  Get the occupants out (egress)
  Get the fire fighters personnel in (ingress)
Fire Protection approach is based on experience from previous projects at the laboratory

## Slide 4: Design
Less than 30 feet below level of exit discharge, omitting the requirements for smoke control and stairway pressurization
Two Exit stairways enclosed by 2 hour fire rated construction
Means to separate Enclosure from Detector Hall
Maximum travel distance 300 feet
Minimum aisle width 36 inches
Automatic fire sprinkler system, preaction type (Detector Hall)
Linear heat type detection
Beam Type Smoke Detection & Spot Type Detection
Air sampling smoke detection
Manual pull stations

## Slide 5: Design Continued
Fire Alarm will have Emergency Voice Alarm system enable to interface with Fermilab’s Site-wide Emergency Warning System
Emergency and exit signage
Emergency/Standby power systems
  Fire alarm system
  Exit signs
  Emergency Lighting
  Elevator
  Sump System

## Slide 6: DESIGN (Site Plan)

## Slide 7: Fire Detection – Main Level

## Slide 8: Fire Detection – Lower Level

## Slide 9: Fire Suppression – Main Level

## Slide 10: Fire Suppression – Main Level

## Slide 11: Design (Section View)

## Slide 12: Design (Detector Hall Detail)