## Slide 1: Operational Status of Decay Volume Helium Vessel at J-PARC Neutrino Experimental Facility
T. Ishida
Neutrino Section, J-PARC Center, KEK
on behalf of the neutrino beam group

## Slide 2: Contents
The Helium Vessel at J-PARC neutrino beam-line
Status of water cooling
Status of Helium atmosphere in the vessel
Summary

## Slide 3: 1. The Helium Vessel at J-PARC neutrino beam-line
Target Station(TS), Decay Volume(DV) & Beam Dump(BD) all enclosed in a gigantic vacuum/helium vessel, made of carbon steel plates.
  Water cooling through plate coils welded on surface
  Upstream cooling system at TS / downstream system at a utility bldg. (NU3)
He gas filling after evacuation
  Entire structures were rigidly built with thick plates (100mm for TS / 16mm + anchors for DV / 200mm for BD), welded together with deep grooves.
He circulation by a helium compressor at TS: Flow rate = ~1,600Nm3/h
  Inlet plays role as coolant of horn strip-line cooling duct.
  No forced circulation for DV/BD (piping at BD exist for future use)
Decay Volume
Target Station
Beam Dump
Vessel filled w 1atm. He gas
L=~110m,V=1,300m3
OA2o
OA2.5o
Beam Transport
From RCS to MLF
6m-thick concrete wall
OA3o

## Slide 4: Helium Vessel at TS
200mm-thick iron plates with
plate coil water paths
Recycled from K2K ND (MRD)
Valves
OTR window
Flanges for the busbar of the horns
Top lids
(3 pieces of 120mm-thick Aluminum )
4.4 m
10.6 m
15.0 m
Target Station: 300t
Upstream DV: 170t in total

## Slide 5: TS/DV Helium Vessel Construction
Upstream DV
Oct.05’07
DV
Support anchors
Embedded in concrete wall
TS
Top lids
(3 pieces of 120mm-thick Aluminum )

## Slide 6: Inside of TS vessel
Photos on Sep., 2009 (before Physics Run)
Horn-2
[downstream]
Horn-3
[upstream]
bus-bar cooling ducts = helium inlet to the vessel
Clearances ~30mm
Plate coils

## Slide 7: Inside of decay volume
  Water circuits are separated to upstream and downstream.
  Each composed of 20 circuits – 40 water channels.
2009/2/27
  downstream end
3.0m
5.1m
2009/9/26
  entrance
1.4m
1.7m
“Plate Coil”
Water cooling
channel
3.2mm
16mm
U-shaped
pipe connection (25A)
BD upstream
inner-vessel shield
Hadron absorber

## Slide 8: Plumbing at muon pit
Control water flow of 260water channels (130 circuits), ~500 Valves (25A)
Though it is designed to use half of the circuits for 750kW beam, we forced to use all channels with low flow rate.
  It may cause troubles for carbon steel, if we remove water from the channels.
  Supply
  header
  Return
  header
  To Decay Volume
  (downstream)
  To BD
  Upstream shield
  To Absorber
  cooling modules
[West side wall]
TP
-12m
TP
-5.1m

## Slide 9: Cooling Water System [NU3: downstream DV+BD]
  Superhot
  machine
  room
  [B1F]
  Hot
  machine
  room
  [1F]
  Tertiary
  Secondary
  Heat
  exch.
  HEX
  Cooling
  towers
  Purified
  water
  supply
  N2 gas
  supply
  for ET
  Outside
  yard
  [GL]
  Expansion
  tank
  Exp. tank
  [Water supplier]
  Ion-exchange resins
  [+ 0.5um Pre-filter]
  ※ NOT USED ※
  It may cause damage
  to carbon steel
  Muon pit
  [B2F]
  Primary
  (irradiated)
  Degasifier
  Hollow fiber membrane
  [+ 0.3um Pre-filter]
  ※ key component ※
  to prevent corrosion
  Industrial
  water
  supply
  Header
  DV/BD
  [B1F+4.5m stand]
  Centrifugal
  pumps
  Hollow
  fiber
  membrane

## Slide 10: 2. Status of Water cooling [after NBI2012]
Pre-filters for the degassifier (5um⇒1um) was installed to TS CW system in summer 2012 (similar system to NU3)
They effectively absorb the radio-active particulate in the water (7Be), but frequently clog up.
  Powder of carbon steel (black skin)
Exchange/tuning of filters caused 8hrs x 2 beam loss in Nov. 2012 runs (Run-4)
New system was installed during the 2012 winter shut-down.
  Remote controls, such as switching to a spare set of reserve filters / opening bypass line, are possible without disturbing beam runs.
Degassifier
Filter A’~D’
Filter A~D

## Slide 11: Decrease of cooling water flow rate at NU3 (Feb.2013)
Drop of cooling water flow rate observed for DV He vessel and beam dump.
The black powder may clog up the water paths / valves.
It was found that flow rate ~0 for some of channels
  After adjusting the flow rate of each channel, flow rate stabilized.
Flow rate decreasing
Pressure at inlet increases
2/16
2/20
2/24
2/26
3/1
Absorber core temperatures
1,100ℓ/min
1,400ℓ/min
62.5℃
0.75MPa
47.5℃
0.6MPa
Tuning
Flow Rate

## Slide 12: Flow rate decrease at degasiffier (NU3) [Mar 2014]
Flow rate <100l/min
(nominal 135)
Pressure after reducing valve 0.1MPa (0.3MPa)
Y-strainer
Reducing valve
(+small strainer)
Y-strainer
Small strainer

## Slide 13: Radioactivity in cooling water (NU3)
Radioactive nuclei in the primary cooling water
  Run-4: Oct. 2012 ~ May. 2013, 3.6x1020pot, -230kW
  On Dec. 2012 we disposed some amount of water to boot up water dilution process and to prepare for the summer maintenance in 2013.
  Only 3H is beyond limit for disposal.
  The 0.3um pleats filters in front of degasiffier seems to be very effective to adsorb/concentrate 7Be
  So far daughters of Fe is not serious problems.
  In sometime future it will be necessary to use ion exchanging resins before drainage.
Spc. | 3H | 7Be | 22Na | 43K | 52Mn | 54Mn
Bq/cc (Dec.2012) | 740 | 1.0 | 0.045 | - | 0.046 | 0.12
Bq/cc (May.2013) | 500 | 1.2 | 0.045 | 0.1 | 0.11 | 0.13
Disp.limit | 60 | 30 | 0.3 | 3 | 0.5 | 1
Life | 12.3y | 53.2d | 2.6y | 22.3h | 5.6d | 312d

## Slide 14: 3. Status of Helium atmosphere in the vessel
By evacuation we reach to <100Pa (0.1%) with a few days ~ a week
  Vacuum was saturated by outgas (20 Pa・m3/s), possibly from vessel surface / concrete shield blocks in the TS vessel
Tiny amount of air leak at BD vessel: 10-2~10-1 Pa・m3/s=1~10ppmO2/day.
  air contamination suppressed by keeping slightly positive pressure wrt. atmosphere.
  O2 contamination < 100ppm for entire beam period
The dew point (humidity) in the vessel was saturated in a week after gas filling
  Source of Tritium (HTO) production
  From concrete surface ? Water leaking ?
  ⇒ From Oct. 2012, we faced to water leak from Horn(s)
Mechanical-booster pumps
@ TS B1 stand
Aggravation rate= 46Pa/h
20 Pa・m3/s
81 Pa
2009
~2days to reach to <100 Pa
He gas filling

## Slide 15: Gas chromatograph measurement [Apr.2013]
On Feb.~Mar.2013 gas chromatograph was installed to TS
  Helium vessel(Apr.2013):
  N2 1,500 ppm
  O2 20 ppm
  CH4 30 ppm
  CO2 /CO 0 ppm
Consistent to the reach of evacuation
Oxygen is low enough.
gas chromatograph at TS-1F
Coolant Helium gas for target, beam window, and He vessel
Cover gas of horn cooling water

## Slide 16: Dried Air Supplier @ NU3
Before opening He vessel, we need to dry up inside of vessel to avoid suffering internal exposure by 3H (HTO).
3H level in the vessel is much higher than that in 2011.
  2011: ~1300mBq/cm3 after 1.4x1020 POT
  2012: ~1100mBq/cm3 after 1.6x1020 POT
  2013: ~1900mBq/cm3 after 3.6x1020 POT
In 2011, it took 3 weeks to reduce 3H level from 1.3Bq/cc to 0.2Bq/cc
We have reinforced dried air supplier at NU3: higher flow rate & lower dew point.
Compressor
2.4m3/min
(was 1m3/min)
400 L
Air
tank
Refrigerated
Air Dryer
Heatless
Air Dryer
(new)
Low dew point
clean air

## Slide 17: Drying He Vessel [Sep. 2013 -]
Vessel evacuation on Sep.12-13, drying vessel by air supplier at NU3 started on Sep.17.
  Dew point >20℃→-20℃,
  3H 1.8 Bq/cc  100mBq/cc (2011: 210mBq/cc)
Vessel was opened on Oct.17 (One month)
Exhaust f
airflow
[m3/h]
P Vessel
[MPa]
P atm
[MPa]
Dew P [degC]
3H [Bq/cc]
0
9/17~20
9/24~27
9/30~10/17

## Slide 18: BD/DV Inspection [Nov.27, 2013]
After old Horn-3 was moved to maintenance area, we set web camera on the beam-line and inspect DV/BD status

## Slide 19
BD/DVは健全

## Slide 22: Horn-2 dew condensation
Imprint of dew condensation was clearly identified at the surface of Horn-2
It was acting as dehumidifier of the helium vessel…

## Slide 23: Imprint of puddle at bottom of TS vessel
Dirty powder layer due to water drainage from horn leak plus dew condensation (?)

## Slide 24: Replacing Heat Exchanger (TS) [Dec.2013]
DP became >0.4MPa, possibly due to clogging of black iron powder
  Residual dose: O(100uSv/h)
We replaced with
new one.
  DP < 0.1MPa

## Slide 25: Source of Vessel Humidity ?
Dew point= 25~26 deg.C.
  Outgas from surface of wall/concrete blocks ?
    Wall: ~3x10-4 Pa・m3/s/m2 → Vessel (1,700m2) 0.6 Pa・m3/s
    Concrete Block: ~1x10-2 Pa・m3/s/m2 → Shield(240m2) 3 Pa・m3/s
    The values are still not so consistent to 20 Pa・m3/s.
    It is curious that the outgas lasts whole the run ?
Run-4: horn water leak = the source of the humidity !
  The humidity cause dew condensation to horns
  It can become critical problem on its performance and life limitation!
During 2013 maintenance we realized many bad SWL connections for the iron shield blocks in the TS vessel.
  We tried to fix them all but not in perfect manner.
  Typical dew point: 14℃(May.28)⇒25℃(Jun.26, 2014)
  ※ For Run-5 we raised up temperature of coolant water to horn H/X and after cooler of He compressors from 22→25℃ (Aug. 2013) to avoid dew condensation (temporal solution)

## Slide 26: Bad SWL connections for iron shields

## Slide 27: Summary
Evacuation and He filling: it takes a week to make vacuum level < 100 Pa (~1,000ppm of air).
  Oxygen < 100 ppm for entire beam periods: prevent NOX production and oxidation of the apparatus inside.
  Validated by gas-chromatograph measurements.
  We successfully used 1st set of horns, target, window, OTR, DV for 5 years.
Due to the saturation of humidity in the vessel helium, before opening vessel to start maintenance, we need to dry HTO.
  We improved the dried air supplier at NU3 and finish the process in a month.
  Situation will be improved by fixing bad SWL connections of shield blocks.
  We raised up horn cooling water temperature to stop dew condensation.
For cooling water circuits (made of carbon steel), powder of iron black skin clogs up filters/HX…/strainers/valves not a few times.
  We continuously reinforce the system (automated filter exchange etc.)

## Slide 28: Test Outgas Measurements
BG 12Pa/h =3.3x10-4 Pa・m3/s/m2 → Vessel (1,700m2) 0.6 Pa・m3/s
Block 47(-12)Pa/h = 1.0x10-2 Pa・m3/s/m2 → Shield(240m2) 3 Pa・m3/s
The values are still not consistent to 20 Pa・m3/s, but maybe comparable.
    Cf. Block weight: 0.023%/d →Shield(130t) 45 Pa・m3/s (assume all vapors remain)
Block w paint
V=6e-3 m3
13 kg
Reduced
-3g /day by
evacuation
N2 gas for purge
Pump
495Φｘ1,000L
V=0.192 m3
S=1.94 m2
60 kg scale
dM =1g

## Slide 29: Cooling water flow at TS
7℃
12℃
31℃
32℃
[radioactive]
From ＮＵ２
ToHorn
CW H/X
Ｈｅ compressors
He compressor (after coolers)
2nd H/X
target
Helium
Vessel
Decay
volume
Iron
shields
22→25℃